# BEACON

BMS data requirements for the energy efficiency dashboard

This document lists the data needed from each building system to build an energy management hypervision: live consumption, efficiency KPIs, cost, waste detection and faults. It covers energy efficiency data only. Maintenance and diagnostic data is listed at the end of each system as "Kept for future maintenance use" and is not required now.

Each system section follows the same structure: Required data, Good to have data, KPIs the dashboard calculates, the Minimum set if the provider can supply only limited data, Static data to collect once, and data kept for future maintenance use.

## Abbreviations

| Term | Meaning |
| --- | --- |
| AHU / FCU / TFA | Air Handling Unit / Fan Coil Unit / Treated Fresh Air unit |
| BTU meter | Thermal energy meter (measures cooling or heating delivered) |
| COP | Coefficient of Performance (energy output ÷ energy input) |
| DG | Diesel Generator |
| DO | Dissolved Oxygen (in the STP aeration tank) |
| EUI | Energy Use Intensity (kWh per m² per year) |
| GRMS / PMS | Guest Room Management System / Property Management System (hotels) |
| IAQ | Indoor Air Quality |
| KLD | Kilolitres per day (1 KLD = 1 m³/day) |
| kWh(th) | Thermal energy in kWh (heat or cooling delivered, not electricity) |
| RO | Reverse Osmosis (water treatment) |
| STP / WTP | Sewage Treatment Plant / Water Treatment Plant |
| TR / TR-h | Tons of Refrigeration (cooling capacity) / TR-hours (cooling energy) |
| VFD | Variable Frequency Drive (motor speed control) |

# Part 1: Systems Overview

## Energy consumers, ranked by usage

Indicative shares for a typical commercial building in a warm climate such as India. Actual shares vary by building type and size; the dashboard will show the real numbers. Section numbers in Part 2 follow this ranking.

| Rank | System | Indicative share of total energy |
| --- | --- | --- |
| 1 | Chiller Plant | 25–40% |
| 2 | Air Handling Units (AHU) and Fan Coil Units (FCU) | 10–15% |
| 3 | Lighting Control System | 10–20% |
| 4 | Ventilation and Exhaust System | 3–8% |
| 5 | Elevator and Escalator System | 3–7% |
| 6 | Boiler / Heating System | 2–8% |
| 7 | Hot Water System | 2–8% |
| 8 | Water Supply System (pumping) | 2–4% |
| 9 | Cold Room / Refrigeration System | 1–5% |
| 10 | UPS System (losses) | 1–3% |
| 11 | Sewage Treatment Plant (STP) | 1–2% |
| 12 | Water Treatment Plant (WTP) | under 1% |
| 13 | Indoor Air Quality (IAQ) Monitoring System | negligible |
| 14 | Life-safety and security systems (Fire, Smoke Control, Gas Leak Detection, Access Control, CCTV, Intrusion Alarm) | negligible |

The HVAC System (ranks 1, 2 and 4 together) typically accounts for 40–60% of a commercial building's energy, so it stays the top priority in any building. IAQ and life-safety systems use almost no energy, but their data (air quality and occupancy) is what reveals waste in the large consumers.

## Energy supply and measurement systems

Not ranked, because they supply or measure energy rather than consume it. They are essential data sources (Sections 15–18).

| System | Role |
| --- | --- |
| Electrical Power Distribution and Energy Metering System | Grid supply, consumption by floor and system, peak demand, power factor |
| Diesel Generator (DG) System | Backup supply; diesel energy and cost |
| Solar / Renewable Energy System | On-site generation that offsets grid use |
| Gas Supply and Metering System | Gas supply to boilers, kitchens, laundry |

## Building-type-specific systems

Present only in some buildings, but large where they exist (Sections 19–22).

| System | Where it matters | Share when present |
| --- | --- | --- |
| Kitchen Equipment | Hotels, hospitals, malls (food courts), campuses | 5–15% |
| Laundry Equipment | Hotels, hospitals | 3–8% |
| Swimming Pool and Spa System | Hotels, clubs, residential complexes | 2–5% |
| Guest Room Management System (GRMS) | Hotels only | Negligible use, but key occupancy data |

# Part 2: Data Requirements by System

# 1. Chiller Plant

The chiller plant is the largest single energy consumer. A water-cooled plant includes the chillers, chilled water pumps, condenser water pumps and cooling towers. Energy comes from chiller meters or a plant sub-meter; cooling delivered comes from a BTU meter, or is calculated from chilled water flow × ΔT.

Required

| Data point | Unit | Why it's needed |
| --- | --- | --- |
| Chiller power / energy | kW, kWh | Energy used by each chiller |
| Pump and cooling tower power / energy (or one total plant sub-meter) | kW, kWh | Whole-plant energy, not just the chillers |
| Chilled water supply temperature | °C | Cooling delivered; setpoint check |
| Chilled water return temperature | °C | Cooling load and ΔT |
| Chilled water flow, or BTU / thermal energy meter | m³/h, or TR / TR-h | Cooling delivered, needed for kW/TR |
| Chiller on/off status and run hours | – / hours | Runtime and after-hours operation |
| Chilled water setpoint | °C | Setpoints colder than needed waste energy |
| Outdoor temperature and humidity | °C, %RH | Weather-normalised comparison |
| Alarm / trip status | – | Explains abnormal consumption |

Good to have

| Data point | Unit | Adds |
| --- | --- | --- |
| Chiller load percentage | % | Part-load and sequencing analysis |
| Number of chillers running | count | Sequencing efficiency |
| Pump and cooling tower fan VFD speed | % or Hz | Whether drives are saving energy |
| Condenser water entering / leaving temperature | °C | Condenser approach and cooling tower performance |
| Heat recovered (if heat recovery is fitted) | kWh(th) | Free heat used for hot water (see Section 7) |

KPIs the dashboard calculates

| KPI | Formula / insight |
| --- | --- |
| Chiller efficiency (kW/TR) | Chiller kW ÷ TR delivered; lower is better; compare with design |
| Plant efficiency (kW/TR) | Total plant kW (chillers + pumps + towers) ÷ TR |
| COP | Cooling output (kW) ÷ electrical input (kW); higher is better |
| Cooling delivered (TR) | Chilled water flow × ΔT |
| Chilled water ΔT (°C) | Return − supply temperature; low ΔT means wasted pumping |
| Specific energy (kWh per TR-h) | Monthly efficiency trend |
| After-hours runtime (hours, kWh) | Plant running outside schedule |
| Chiller plant share of total energy (%) | Comparison with other systems |

Minimum set if the provider can give only a little: plant power and energy, chiller on/off and run hours, chilled water supply/return temperatures, chilled water flow or BTU meter, and alarms. That's enough to calculate kW/TR, the most important chiller efficiency KPI.

Static data to collect once: the chiller list with type (water- or air-cooled), rated capacity (TR), rated power (kW) and design kW/TR; the pump and cooling tower list with rated power (kW); and a plant schematic showing which meter measures what.

Kept for future maintenance use: compressor current, refrigerant pressures, number of starts, differential pressure, cooling tower make-up water, vibration and oil condition.

# 2. Air Handling Units (AHU) and Fan Coil Units (FCU)

AHUs and FCUs are listed separately because they're monitored differently. AHUs are large central units with their own meters and sensors. FCUs are small, numerous room units, usually without individual power meters.

## 2.1 Air Handling Units (AHU / TFA)

Required

| Data point | Unit | Why it's needed |
| --- | --- | --- |
| Fan power / energy | kW, kWh | Energy used by each AHU |
| On/off status | On / Off | When the unit is running |
| Run hours | hours | After-hours runtime and waste |
| Supply air temperature | °C | Whether air is being over-cooled |
| Supply air setpoint | °C | Setpoints colder than needed waste energy |
| Return air temperature | °C | Cooling load from the space |
| Fan speed (VFD) | % or Hz | Whether drives are saving energy or stuck at 100% |
| Operating schedule | time | Detects running outside occupied hours |
| Alarm / trip status | – | Explains abnormal consumption |

Good to have

| Data point | Unit | Adds |
| --- | --- | --- |
| Chilled water valve position | % | Cooling demand; valve stuck open |
| Fresh air damper position | % | Too much outside air raises cooling energy |
| Return air CO₂ | ppm | Ventilation matched to occupancy |
| Return air humidity | %RH | Dehumidification load |

## 2.2 Fan Coil Units (FCU)

Required

| Data point | Unit | Why it's needed |
| --- | --- | --- |
| On/off status | On / Off | Running time per room |
| Fan speed | Low / Med / High or % | Energy is estimated from fan speed |
| Room temperature | °C | Comfort and over-cooling |
| Room setpoint | °C | Setpoints too low waste energy |
| Mode | Cool / Heat / Fan / Off | Correct operation |
| Occupancy status | Occupied / vacant | AC running in empty rooms |
| Energy (floor or zone sub-meter) | kWh | FCU energy, since single FCUs rarely have meters |

Good to have

| Data point | Unit | Adds |
| --- | --- | --- |
| Chilled water valve status / position | % or Open / Closed | Actual cooling demand |
| Room humidity | %RH | Comfort and condensation risk |

KPIs the dashboard calculates

| KPI | Insight |
| --- | --- |
| AHU / FCU energy (kWh) per floor or zone | Where air-side energy goes |
| Air-side share of total HVAC energy | Balance between chiller and fans |
| After-hours runtime (hours, kWh) | Units running outside schedule |
| Units running in vacant rooms | Direct waste |
| Supply air over-cooling | Supply temperature or setpoint lower than needed |
| Average room setpoint | Rooms set too cold (each 1 °C lower adds roughly 6–8% to cooling energy) |
| VFD savings | Fan speed vs full speed |
| Comfort compliance | % of time rooms are inside the comfort band |

Minimum set if the provider can give only a little: AHU fan energy, AHU and FCU on/off status with run hours, supply air temperature and setpoint, room temperature and setpoint, and occupancy. That's enough to show air-side energy, after-hours waste, and AC running in empty rooms.

Static data to collect once: the AHU and FCU list with location, the floor/zone/room each unit serves, rated fan power (kW) and cooling capacity (TR or kW). FCU energy estimates depend on the rated power at each fan speed.

Kept for future maintenance use: filter differential pressure, fan belt and bearing condition, vibration, coil condition and actuator faults.

# 3. Lighting Control System

Lighting is usually controlled by zones or circuits (a floor area, corridor or room group), not by individual fittings, so data is collected at that level. Energy normally comes from lighting panel sub-meters; where those aren't available, it's estimated from connected load × on-time × dim level.

## 3.1 Indoor Lighting (zones / circuits)

Required

| Data point | Unit | Why it's needed |
| --- | --- | --- |
| Lighting energy per floor / panel (sub-meter) | kWh | Actual lighting consumption |
| Lighting power per floor / panel | kW | Live load and peak |
| On/off status per zone or circuit | On / Off | When lights are running |
| Run hours per zone | hours | After-hours lighting waste |
| Occupancy status per zone | Occupied / vacant | Lights on in empty areas |
| Lighting schedule per zone | time | Lights on outside planned hours |

Good to have

| Data point | Unit | Adds |
| --- | --- | --- |
| Dimming level | % | Real energy when lights are dimmed |
| Daylight level (daylight sensors) | lux | Lights on when daylight is enough |
| Manual override status | Auto / Manual | Overrides defeating automatic savings |

## 3.2 External / Facade / Signage / Car Park Lighting

Required

| Data point | Unit | Why it's needed |
| --- | --- | --- |
| Energy (sub-meter) | kWh | External lighting consumption |
| On/off status and run hours | – / hours | Lights on during daytime |
| Schedule or astronomical timer setting | time | Correct on/off times |

Good to have

| Data point | Unit | Adds |
| --- | --- | --- |
| Outdoor light level (photocell) | lux | Lights switched on too early or off too late |

KPIs the dashboard calculates

| KPI | Insight |
| --- | --- |
| Lighting energy per floor / zone (kWh) | Where lighting energy goes |
| Lighting share of total building energy (%) | Lighting vs other systems |
| Lighting power density (W/m²) | Compares floors and buildings; flags inefficient fittings |
| Lighting energy intensity (kWh/m²) | Comparison over time and across buildings |
| After-hours lighting (hours, kWh) | Lights on outside schedule |
| Lights on in vacant zones (hours, kWh) | Direct waste |
| Daytime external lighting (hours) | Facade or car park lights on in daylight |
| Daylight savings achieved (%) | Benefit of daylight dimming |
| Override frequency | Where people disable automatic control |

Minimum set if the provider can give only a little: lighting energy per floor or panel, on/off status and run hours per zone, occupancy per zone, schedules, and external lighting on/off. That's enough to show lighting consumption, after-hours waste, and lights on in empty areas.

Static data to collect once: the zone list with area (m²) and connected load (kW) per zone. Without it, lighting power density and energy estimates aren't possible.

Kept for future maintenance use: lamp and driver failures, burning hours for replacement planning, and lighting controller faults.

# 4. Ventilation and Exhaust System

Covers: toilet exhaust, kitchen exhaust, basement / car park ventilation and fresh air fans. Individual fans rarely have meters, so energy usually comes from group sub-meters, or is estimated from rated power × run hours × speed.

Staircase and lift pressurisation fans are excluded from energy analysis. They're life-safety equipment that runs only during a fire or a test. Their run status is used only to explain unusual fan energy during tests or fires (see Section 14).

## 4.1 General Exhaust and Fresh Air Fans (toilets, plant rooms, stores)

Required

| Data point | Unit | Why it's needed |
| --- | --- | --- |
| Energy (group sub-meter) | kWh | Ventilation consumption |
| On/off status per fan or group | On / Off | When fans are running |
| Run hours | hours | Fans running 24/7 unnecessarily |
| Operating schedule | time | Running outside occupied hours |
| Fan speed (if VFD or multi-speed) | % or Hz | Energy savings from speed control |

## 4.2 Kitchen Exhaust and Make-up Air

Required

| Data point | Unit | Why it's needed |
| --- | --- | --- |
| Exhaust and make-up air fan energy | kWh | Kitchen ventilation consumption, often large |
| On/off status and run hours | – / hours | Fans left running after the kitchen closes |
| Fan speed | % or Hz | Demand-controlled ventilation savings |
| Kitchen operating hours | time | Running outside cooking hours |

Good to have

| Data point | Unit | Adds |
| --- | --- | --- |
| Hood temperature / cooking activity sensor | °C or status | Matches fan speed to actual cooking load |

## 4.3 Basement / Car Park Ventilation (jet fans, supply and exhaust fans)

Required

| Data point | Unit | Why it's needed |
| --- | --- | --- |
| Fan energy (group sub-meter) | kWh | Car park ventilation consumption |
| On/off status and run hours | – / hours | Fans running when not needed |
| Fan speed / stage | % or stage | Speed vs actual demand |
| CO level | ppm | Fans should run by pollution level, not continuously |

Good to have

| Data point | Unit | Adds |
| --- | --- | --- |
| NO₂ level | ppm | Better demand control (diesel vehicles) |

KPIs the dashboard calculates

| KPI | Insight |
| --- | --- |
| Ventilation energy by group (kWh) | Where fan energy goes |
| Ventilation share of total energy (%) | Comparison with other systems |
| After-hours fan runtime (hours, kWh) | Fans running outside schedule |
| Fans running at full speed with low CO / CO₂ | Demand control not working; direct waste |
| Kitchen exhaust running after closing | Common, easy-to-fix waste |
| Average fan speed vs full speed (%) | VFD savings achieved |

Minimum set if the provider can give only a little: group energy sub-meters, on/off status and run hours per fan group, schedules, and CO level in the car park. That's enough to show ventilation consumption, after-hours waste, and car park fans running without need.

Static data to collect once: the fan list with location, group and rated power (kW). It's needed to estimate energy where meters aren't installed.

Kept for future maintenance use: fan belt and bearing condition, vibration, motor temperature and filter condition.

# 5. Elevator and Escalator System

Elevators and escalators are usually monitored through the manufacturer's monitoring system or a gateway (Otis, Schindler, KONE, Thyssenkrupp), so the available data depends on what that interface exposes. Energy normally comes from sub-meters per elevator bank or escalator panel.

## 5.1 Elevators

Required

| Data point | Unit | Why it's needed |
| --- | --- | --- |
| Energy per elevator or elevator bank (sub-meter) | kWh | Elevator consumption |
| Power | kW | Live and peak load |
| Operating status | Running / Idle / Standby | Time spent idle with full power |
| Number of trips | count | Energy per trip, usage pattern |
| Operating schedule / mode | Normal / Off-peak / Parking | Too many elevators active at night |

Good to have

| Data point | Unit | Adds |
| --- | --- | --- |
| Standby / sleep mode status | On / Off | Whether car lights and fans switch off when idle |
| Regenerated energy (regenerative drives) | kWh | Energy returned to the building |
| In service / out of service | – | Explains drops in consumption |

## 5.2 Escalators and Travelators

Required

| Data point | Unit | Why it's needed |
| --- | --- | --- |
| Energy per escalator or group (sub-meter) | kWh | Escalator consumption |
| Running status | Running / Stopped | When escalators run |
| Run hours | hours | Running outside building hours |
| Speed mode | Normal / Slow / Stop | Whether standby (slow) mode is used |
| Operating schedule | time | Running before opening or after closing |

Good to have

| Data point | Unit | Adds |
| --- | --- | --- |
| Passenger detection / footfall | count | Escalators running empty at full speed |

KPIs the dashboard calculates

| KPI | Insight |
| --- | --- |
| Vertical transport energy (kWh) and share of total (%) | Comparison with other systems |
| Energy per elevator trip (kWh/trip) | Elevator efficiency; comparison between elevators |
| Idle / standby energy share (%) | Energy wasted when elevators aren't moving |
| Elevators in service at night vs needed | Too many elevators active off-peak |
| Escalator after-hours runtime (hours, kWh) | Running outside opening hours |
| Escalator time running empty at full speed | Standby mode not used |

Minimum set if the provider can give only a little: energy sub-meter per elevator bank and escalator group, run status and run hours, and operating schedules. That's enough to show vertical transport consumption and after-hours waste.

Static data to collect once: the list of elevators and escalators with location, rated motor power (kW) and drive type (regenerative or not).

Kept for future maintenance use: fault codes, door cycles, levelling errors and breakdown history.

# 6. Boiler / Heating System

Heating can come from hot water boilers, steam boilers or heat pumps, fuelled by gas, diesel or electricity. In India, heating is mostly used for hot water, kitchens and laundry, and for space heating in colder regions. Energy comes from fuel meters (gas, diesel) or electrical sub-meters, and heat output from heat or steam meters.

## 6.1 Hot Water Boilers

Required

| Data point | Unit | Why it's needed |
| --- | --- | --- |
| Fuel consumption | m³ (gas), litres (diesel), kWh (electric) | Energy input |
| Heat output (heat meter) | kWh(th) | Energy delivered, for boiler efficiency |
| Supply water temperature | °C | Heat delivered |
| Return water temperature | °C | Heat load and ΔT |
| Supply temperature setpoint | °C | Water heated more than needed |
| On/off status | On / Off | When the boiler runs |
| Run hours | hours | After-hours or unnecessary operation |
| Firing rate / modulation | % | Part-load efficiency, cycling |
| Hot water pump power / energy | kW, kWh | Pumping energy |

Good to have

| Data point | Unit | Adds |
| --- | --- | --- |
| Flue gas temperature | °C | Combustion efficiency |
| Flue gas O₂ | % | Excess-air losses |
| Number of burner starts | count | Short-cycling, which wastes fuel |
| Hot water flow | m³/h | Heat output where no heat meter exists |

## 6.2 Steam Boilers (hotels, hospitals, laundries, kitchens)

Required

| Data point | Unit | Why it's needed |
| --- | --- | --- |
| Fuel consumption | m³, litres, kWh | Energy input |
| Steam output / flow | kg/h or tonnes | Energy delivered |
| Steam pressure | bar | Operating condition |
| Feed water temperature | °C | Heat-recovery effectiveness |
| On/off status and run hours | – / hours | Runtime |

Good to have

| Data point | Unit | Adds |
| --- | --- | --- |
| Condensate return flow / temperature | m³, °C | Heat recovered (unreturned condensate is energy lost) |
| Flue gas temperature and O₂ | °C, % | Combustion efficiency |

## 6.3 Heat Pumps

If a heat pump only makes domestic hot water, count it under Section 7 (Hot Water) instead. Each heat pump's energy is counted once, under the system it serves.

Required

| Data point | Unit | Why it's needed |
| --- | --- | --- |
| Electrical energy / power | kWh, kW | Energy input |
| Heat output (heat meter) | kWh(th) | Energy delivered, for COP |
| Supply and return water temperature | °C | Heat delivered |
| Setpoint | °C | Overheating waste |
| On/off status and run hours | – / hours | Runtime |

KPIs the dashboard calculates

| KPI | Formula / insight |
| --- | --- |
| Boiler efficiency (%) | Heat output ÷ fuel energy input |
| Heat pump COP | Heat output ÷ electrical input |
| Fuel energy converted to kWh | Gas m³ or diesel litres → kWh, for total building energy |
| Heating share of total energy (%) | Comparison with other systems |
| Heating energy per m² or per occupied room | Comparison across buildings |
| Weather-normalised heating (heating degree days) | Fair month-to-month comparison |
| Short-cycling rate (starts per hour) | Fuel wasted by frequent on/off |
| Heating cost (₹ or €) | Fuel × tariff |

Minimum set if the provider can give only a little: fuel or electricity consumption, supply/return temperatures, setpoint, on/off status and run hours, and a heat meter if one exists. That's enough to show heating consumption, cost, after-hours waste and an estimated efficiency.

Static data to collect once: the boiler / heat pump list with type, fuel, rated capacity (kW or kg/h steam) and design efficiency.

Kept for future maintenance use: burner faults, water chemistry (TDS, pH), blowdown, safety valve and flame failure alarms.

# 7. Hot Water System

The hot water system covers producing, storing and distributing hot water to washrooms, guest rooms, kitchens and laundries. Heat can come from boilers, heat pumps, electric heaters, solar thermal panels, or heat recovered from chillers.

If the hot water comes from the boilers in Section 6, count their fuel only once, there. This section then covers storage, distribution and how much hot water is used. The same applies to heat recovered from chillers (Section 1).

## 7.1 Hot Water Generation (energy input)

Required

| Data point | Unit | Why it's needed |
| --- | --- | --- |
| Energy input per source | kWh (electric, heat pump), m³ (gas) | Energy used to make hot water |
| Heat delivered (heat meter, if present) | kWh(th) | Efficiency of each source |
| On/off status and run hours per heater / heat pump | – / hours | Heaters running without demand |
| Heater / heat pump setpoint | °C | Water heated more than needed |

Good to have

| Data point | Unit | Adds |
| --- | --- | --- |
| Solar thermal heat delivered | kWh(th) | Free renewable contribution |
| Heat recovered from chillers | kWh(th) | Recovered energy that replaces fuel |

## 7.2 Storage Tanks (calorifiers)

Required

| Data point | Unit | Why it's needed |
| --- | --- | --- |
| Tank water temperature | °C | Overheating and standby losses |
| Tank setpoint | °C | Correct storage temperature |

The storage temperature can't simply be lowered to save energy. It must stay around 60 °C to prevent Legionella bacteria. The dashboard should flag temperatures above what's needed, not push them below the safe level.

## 7.3 Distribution and Recirculation

Required

| Data point | Unit | Why it's needed |
| --- | --- | --- |
| Hot water consumption (flow meter) | m³ or litres | How much hot water is used |
| Supply temperature to building | °C | Delivery temperature |
| Recirculation return temperature | °C | Heat lost in the pipework |
| Recirculation pump on/off status and run hours | – / hours | Pumps running 24/7 unnecessarily |
| Recirculation pump energy | kWh | Pumping energy |

KPIs the dashboard calculates

| KPI | Insight |
| --- | --- |
| Hot water energy (kWh) and share of total (%) | Comparison with other systems |
| Energy per m³ of hot water (kWh/m³) | Overall hot water efficiency |
| Hot water use per occupant / occupied room / meal | Usage benchmarking |
| Distribution heat loss | Supply vs recirculation return temperature; poor pipe insulation |
| Renewable / recovered share (%) | Solar thermal and heat recovery vs fuel |
| Overheating time (hours above setpoint) | Energy wasted heating water too much |
| Recirculation pump after-hours runtime | Pumps running when no one uses hot water |
| Hot water cost (₹ or €) | Energy × tariff |

Minimum set if the provider can give only a little: energy input per source, hot water consumption (flow meter), tank temperature and setpoint, supply and recirculation return temperatures, and recirculation pump status. That's enough to show hot water energy, energy per m³, distribution losses and overheating.

Static data to collect once: the list of heaters, heat pumps and tanks with type, energy source, rated capacity (kW) and tank volume (litres).

Kept for future maintenance use: scale build-up, anode condition, leaks, pressure relief valve operation and Legionella flushing records.

# 8. Water Supply System (pumping)

The water supply system moves water from the source (municipal supply, borewell or tanker) into storage (underground sump, overhead tanks) and on to users through transfer, booster or hydropneumatic pumps. Energy comes from pump sub-meters, and water quantity from water meters.

Fire pumps are excluded. They're life-safety equipment and only run during a fire or a test.

## 8.1 Pumps (transfer, booster, hydropneumatic, borewell)

Required

| Data point | Unit | Why it's needed |
| --- | --- | --- |
| Pump energy (per pump or pump-room sub-meter) | kWh | Pumping energy |
| Pump power | kW | Live load |
| On/off status per pump | On / Off | When pumps run |
| Run hours per pump | hours | Excess running, imbalance between pumps |
| Pump speed (VFD) | % or Hz | Energy savings from speed control |
| Header / delivery pressure | bar | Pressure higher than needed wastes energy |
| Pressure setpoint | bar | Correct pressure target |

## 8.2 Water Flow and Storage

Required

| Data point | Unit | Why it's needed |
| --- | --- | --- |
| Water consumption, main meter | m³ | Total water used |
| Water pumped per pump set | m³ | Energy per m³ pumped |
| Water by source (municipal, borewell, tanker) | m³ | Source mix and cost |
| Sump and overhead tank levels | % or m | Pumps running against full tanks; overflow |

Good to have

| Data point | Unit | Adds |
| --- | --- | --- |
| Water sub-meters by use (domestic, flushing, cooling tower make-up, kitchen, laundry, landscape) | m³ | Where water goes |
| Tank overflow alarm | – | Water and pumping energy wasted |

KPIs the dashboard calculates

| KPI | Insight |
| --- | --- |
| Pumping energy (kWh) and share of total (%) | Comparison with other systems |
| Specific pumping energy (kWh/m³) | Pump efficiency; comparison between pump sets |
| Water use intensity (m³ per m², occupant or occupied room) | Water benchmarking |
| Night flow (consumption at 2–4 AM) | Leak detection: steady flow when the building is empty |
| Pumps running with a full tank, or overflow events | Direct water and energy waste |
| Pressure above setpoint | Over-pressurisation wastes energy and water |
| Water cost by source (₹ or €) | Tanker water is far costlier than municipal supply |

Minimum set if the provider can give only a little: pump energy (pump-room sub-meter), pump on/off status and run hours, main water meter, and tank levels. That's enough to show pumping energy, kWh per m³, overflow waste, and leaks via night flow.

Static data to collect once: the list of pumps with location, purpose and rated power (kW), plus tank capacities (litres or m³) and water tariffs per source.

Kept for future maintenance use: dry-run protection trips, vibration, seal and bearing condition, and motor temperature.

# 9. Cold Room / Refrigeration System

Refrigeration covers chilled cold rooms (around +2 to +8 °C), freezer rooms (around −18 to −25 °C) and, in larger sites, central refrigeration racks that serve several rooms. They run 24/7, so even small waste adds up. Energy comes from sub-meters per cold room or refrigeration plant.

For food storage, food safety comes first. The dashboard should flag over-cooling and waste, but never encourage temperatures warmer than the safe limit.

## 9.1 Each Cold Room / Freezer

Required

| Data point | Unit | Why it's needed |
| --- | --- | --- |
| Energy (per room or condensing unit) | kWh | Refrigeration consumption |
| Power | kW | Live load |
| Room temperature | °C | Over-cooling and safe range |
| Room setpoint | °C | Rooms set colder than needed |
| Compressor on/off status | On / Off | Running pattern |
| Compressor run hours / duty cycle | hours, % | Room struggling to hold temperature |
| Door open status | Open / Closed | Doors left open are the biggest cause of waste |
| Door open duration | minutes | Total cold lost per day |
| Defrost status | On / Off | Defrost heaters use significant energy |

Good to have

| Data point | Unit | Adds |
| --- | --- | --- |
| Number of defrost cycles | count | Too-frequent defrost wastes energy |
| Evaporator fan status | On / Off | Fans running during defrost or with the door open |
| Ambient temperature at the condensing unit | °C | Hot locations lower efficiency |
| Door heater / anti-sweat heater status (freezers) | On / Off | Heaters running continuously |

## 9.2 Central Refrigeration Plant / Racks (where present)

Required

| Data point | Unit | Why it's needed |
| --- | --- | --- |
| Plant energy (sub-meter) | kWh | Total refrigeration consumption |
| Number of compressors running | count | Staging efficiency |
| Compressor run hours | hours | Load balance |
| Condenser fan status / speed | On / Off, % | Heat-rejection energy |

KPIs the dashboard calculates

| KPI | Insight |
| --- | --- |
| Refrigeration energy (kWh) and share of total (%) | Comparison with other systems |
| Energy per cold room (kWh/day) | Which rooms consume most |
| Energy intensity (kWh per m³ of room volume) | Fair comparison between rooms |
| Compressor duty cycle (%) | High duty means poor insulation, door problems or overload |
| Door open time per day | Main behavioural waste |
| Over-cooling time (hours below setpoint band) | Energy wasted cooling too much |
| Defrost energy share (%) | Defrost settings too frequent or too long |
| Temperature excursions above safe limit | Food safety alert (also explains energy spikes) |

Minimum set if the provider can give only a little: energy per cold room or plant, room temperature and setpoint, compressor on/off and run hours, and door open status. That's enough to show refrigeration energy, duty cycle, door-open waste and over-cooling.

Static data to collect once: the list of cold rooms and freezers with type, volume (m³), target temperature range, condensing unit rated power (kW) and refrigerant type.

Kept for future maintenance use: refrigerant pressures and leak detection, superheat and subcooling, compressor faults and evaporator icing.

# 10. UPS System (losses)

A UPS keeps critical loads (servers, IT, security systems, emergency lighting) running during power cuts. It consumes energy itself as losses: the difference between the power going in and the power coming out. These losses also turn into heat, which the UPS room's AC then has to remove, so they count twice. Data usually comes from the UPS's own communication card (SNMP or Modbus) or from input and output meters.

Required

| Data point | Unit | Why it's needed |
| --- | --- | --- |
| Input power | kW | Power drawn from the grid |
| Input energy | kWh | Energy drawn over time |
| Output power | kW | Power delivered to critical loads |
| Output energy | kWh | Energy delivered over time |
| Load percentage | % | UPS efficiency drops sharply at low load |
| Operating mode | Online / Eco / Bypass / Battery | Eco mode saves energy; bypass and battery explain consumption changes |

Good to have

| Data point | Unit | Adds |
| --- | --- | --- |
| UPS room AC energy | kWh | Cooling energy needed to remove UPS heat |
| UPS room temperature | °C | Over-cooled UPS rooms waste AC energy |
| Time on battery | minutes | Power-cut duration; context for DG operation |

KPIs the dashboard calculates

| KPI | Formula / insight |
| --- | --- |
| UPS losses (kWh) | Input energy − output energy |
| UPS efficiency (%) | Output ÷ input × 100 |
| Loss share of total building energy (%) | Size of the opportunity |
| Average load (%) | Under-loaded UPS units (common in N+1 or 2N redundant setups) |
| Time in eco mode vs online mode (%) | Use of energy-saving mode where allowed |
| Total cost of UPS losses (₹ or €) | Losses × tariff, including the extra cooling |
| Critical load trend (kW) | Growth of IT and critical load over time |

Minimum set if the provider can give only a little: input and output energy (kWh), load percentage and operating mode. That's enough to show UPS losses, efficiency and under-loading.

Static data to collect once: the list of UPS units with location, rated capacity (kVA / kW), type (online / line-interactive), redundancy setup (N, N+1, 2N), connected loads, and the manufacturer's efficiency at different loads.

Kept for future maintenance use: battery voltage, state of charge, battery temperature, battery health / age, fan and capacitor condition, and alarm history.

# 11. Sewage Treatment Plant (STP)

An STP treats the building's wastewater so it can be safely discharged or reused (for toilet flushing, landscaping or cooling tower make-up). The biggest energy user inside an STP is the aeration blowers, often around half of the plant's energy, followed by the pumps. Energy comes from the STP panel sub-meter and individual equipment status.

## 11.1 Aeration Blowers (largest load)

Required

| Data point | Unit | Why it's needed |
| --- | --- | --- |
| Blower energy | kWh | Main STP consumption |
| Blower on/off status and run hours | – / hours | Blowers running more than needed |
| Blower speed (VFD) | % or Hz | Speed matched to demand |
| Dissolved oxygen (DO) in aeration tank | mg/L | DO above target means over-aeration, wasting energy |
| DO setpoint / target | mg/L | Correct aeration target |

## 11.2 Pumps (raw sewage, transfer, filter feed, treated water, sludge)

Required

| Data point | Unit | Why it's needed |
| --- | --- | --- |
| Pump energy (group sub-meter) | kWh | Pumping energy |
| Pump on/off status and run hours | – / hours | Pumps running unnecessarily |

## 11.3 Plant Level

Required

| Data point | Unit | Why it's needed |
| --- | --- | --- |
| Total STP energy (panel sub-meter) | kWh | Whole-plant consumption |
| Sewage inflow | m³ or KLD | Plant load |
| Treated water output | m³ or KLD | Energy per m³ treated |
| Treated water reused (flushing, landscaping, cooling tower) | m³ | Water recycled; fresh water saved |

Good to have

| Data point | Unit | Adds |
| --- | --- | --- |
| UV / disinfection unit status and energy | On / Off, kWh | Units running when the plant isn't treating water |
| Equalisation tank level | % or m | Plant load balance, pump scheduling |

KPIs the dashboard calculates

| KPI | Insight |
| --- | --- |
| STP energy (kWh) and share of total (%) | Comparison with other systems |
| Specific energy (kWh per m³ treated) | Plant efficiency; comparison between buildings |
| Blower share of STP energy (%) | Aeration optimisation potential |
| Over-aeration time (DO above target) | Direct blower energy waste |
| Plant utilisation (% of design capacity) | Oversized or under-used plant |
| Water recycled (%) | Treated water reused vs fresh water consumed |
| Fresh water and cost saved by reuse | Value of recycling (₹ or €) |

Minimum set if the provider can give only a little: total STP energy, blower status and run hours, sewage inflow or treated water output, and treated water reused. That's enough to show STP energy, kWh per m³ and water recycling.

Static data to collect once: STP design capacity (KLD), treatment technology (SBR, MBBR, MBR, etc.) and the equipment list with rated power (kW) for blowers and pumps.

Kept for future maintenance and compliance use: BOD, COD, TSS, pH, MLSS, sludge levels and pollution control board compliance records.

# 12. Water Treatment Plant (WTP)

A WTP treats raw water (borewell, municipal or tanker) so it's fit for drinking, cooking, cooling towers, boilers and laundry. In buildings it usually includes filters (sand and carbon), water softeners and often an RO (reverse osmosis) plant. The RO high-pressure pump is usually the biggest energy user. RO also rejects a share of the water as waste, so the WTP matters for both energy and water efficiency.

## 12.1 RO Plant (largest load)

Required

| Data point | Unit | Why it's needed |
| --- | --- | --- |
| High-pressure pump energy | kWh | Main WTP consumption |
| High-pressure pump on/off status and run hours | – / hours | Running time vs water produced |
| Feed water flow | m³ | Water entering the RO |
| Permeate (treated water) flow | m³ | Useful water produced |
| Reject water flow | m³ | Water wasted |

Good to have

| Data point | Unit | Adds |
| --- | --- | --- |
| RO feed pressure | bar | Pressure higher than needed wastes pump energy |
| Reject water reused (gardening, flushing) | m³ | Waste water recovered |

## 12.2 Filters, Softeners and Pumps

Required

| Data point | Unit | Why it's needed |
| --- | --- | --- |
| Filter feed / transfer pump energy (group sub-meter) | kWh | Pumping energy |
| Pump on/off status and run hours | – / hours | Pumps running unnecessarily |
| Backwash water used | m³ | Water used to clean filters |

Good to have

| Data point | Unit | Adds |
| --- | --- | --- |
| Softener regeneration count | count | Excess regeneration wastes water and salt |
| UV unit status and energy | On / Off, kWh | UV running with no flow |

## 12.3 Plant Level

Required

| Data point | Unit | Why it's needed |
| --- | --- | --- |
| Total WTP energy (panel sub-meter) | kWh | Whole-plant consumption |
| Raw water input | m³ | Plant load |
| Treated water output | m³ | Energy per m³ treated |

KPIs the dashboard calculates

| KPI | Insight |
| --- | --- |
| WTP energy (kWh) and share of total (%) | Comparison with other systems |
| Specific energy (kWh per m³ treated) | Plant efficiency |
| RO recovery (%) | Permeate ÷ feed; low recovery means more water wasted |
| Reject water (m³ and %) | Water wasted by RO |
| Backwash water share (%) | Excessive filter cleaning |
| Plant utilisation (% of design capacity) | Oversized or under-used plant |
| Water loss in treatment (%) | Raw water in vs treated water out |

Minimum set if the provider can give only a little: total WTP energy, raw water input and treated water output, RO permeate and reject flows, and pump on/off status and run hours. That's enough to show WTP energy, kWh per m³, RO recovery and water wasted.

Static data to collect once: WTP design capacity (m³/day or KLD), treatment stages (filters, softener, RO, UV) and the equipment list with rated power (kW).

Kept for future maintenance and water-quality use: TDS, hardness, pH, chlorine levels, membrane differential pressure, filter condition, chemical dosing levels and salt levels.

# 13. Indoor Air Quality (IAQ) Monitoring System

IAQ sensors use almost no energy themselves. Their value for the dashboard is context: they show whether HVAC and ventilation energy is being used correctly. They answer two questions:

- Are we over-ventilating or over-cooling (wasting energy)?

- Are we saving energy at the cost of comfort and health?

Each IAQ sensor must be linked to its zone and to the AHU or FCU serving it. Without that link, the data can't be connected to energy.

Required

| Data point | Unit | Why it's needed |
| --- | --- | --- |
| CO₂ | ppm | Shows real occupancy and fresh-air need; low CO₂ with high fresh air means wasted energy |
| Temperature | °C | Comfort; detects over-cooling |
| Relative humidity | %RH | Comfort; dehumidification load |

Good to have

| Data point | Unit | Adds |
| --- | --- | --- |
| PM2.5 / PM10 | µg/m³ | Ensures energy savings don't harm air quality; filter performance |
| TVOC | ppb or µg/m³ | Indoor pollutants that need ventilation |
| Formaldehyde (HCHO) | ppb or µg/m³ | New furniture and fit-outs |
| CO (car parks, kitchens) | ppm | Demand control for exhaust fans (also covered in Section 4) |

KPIs the dashboard calculates

| KPI | Insight |
| --- | --- |
| Over-ventilation time | Low CO₂ (e.g. under 600 ppm) while fresh air or fans run high: energy waste |
| Under-ventilation time | High CO₂ (e.g. over 1,000 ppm): poor air quality; ventilation needs increasing |
| Over-cooling time | Room temperature below the comfort band: HVAC energy waste |
| Comfort compliance (%) | Time temperature and humidity stay inside the comfort band |
| IAQ compliance (%) | Time CO₂, PM2.5 and TVOC stay within limits |
| Estimated occupancy | Derived from CO₂ trends where no occupancy sensors exist |
| Energy vs IAQ balance | Zones that use more energy without better air quality |

The two CO₂ thresholds work together: 600–1,000 ppm is the target band for occupied spaces. Below 600 ppm while ventilation runs high suggests energy is being wasted; above 1,000 ppm means ventilation is not enough.

Minimum set if the provider can give only a little: CO₂, temperature and humidity per zone, mapped to the AHU or FCU serving that zone. That's enough to detect over-ventilation, over-cooling and comfort compliance.

Static data to collect once: the sensor list with location, zone, and the AHU/FCU serving each zone, plus the comfort and IAQ limits to use (for example, temperature 23–26 °C, humidity 40–60%, CO₂ 600–1,000 ppm, or the building's own standards).

Kept for future maintenance use: sensor calibration dates, sensor drift detection and sensor communication faults.

# 14. Life-safety and Security Systems

Fire alarm, smoke control, gas leak detection, access control, CCTV and intrusion alarm systems. Their own energy use is negligible, so the dashboard doesn't need their detailed data. A few of their signals are useful as context for energy: mainly for occupancy and for explaining unusual consumption.

All of this data must be read-only. The energy platform should never send commands to safety systems.

## 14.1 Fire Alarm System

| Data point | Unit | Why it's needed |
| --- | --- | --- |
| Fire alarm active status | Active / Normal | Explains sudden HVAC shutdowns and fan runs during alarms or drills |
| Test / drill mode | On / Off | Excludes test periods from energy analysis |

## 14.2 Smoke Control System

| Data point | Unit | Why it's needed |
| --- | --- | --- |
| Smoke fan / pressurisation fan run status | On / Off | Explains extra fan energy during tests or alarms |
| Smoke control energy (if sub-metered) | kWh | Separates test energy from normal ventilation |

## 14.3 Gas Leak Detection System

| Data point | Unit | Why it's needed |
| --- | --- | --- |
| Gas leak alarm status | Alarm / Normal | Safety alert on the dashboard |
| Gas shut-off valve status | Open / Closed | Explains gas consumption dropping to zero |

## 14.4 Access Control System (most useful of the group)

| Data point | Unit | Why it's needed |
| --- | --- | --- |
| People entering / leaving per building or floor | count | Real occupancy, for energy per occupant |
| Floor or zone occupancy count | count | AC and lighting on in empty floors |
| First entry / last exit time per day | time | Actual building hours vs HVAC and lighting schedules |

## 14.5 CCTV / Video Surveillance

| Data point | Unit | Why it's needed |
| --- | --- | --- |
| People counting (if video analytics exist) | count | Occupancy where access control doesn't count people |

Only anonymous counts should be used here, never images or personal data.

## 14.6 Intrusion Alarm System

| Data point | Unit | Why it's needed |
| --- | --- | --- |
| Armed / disarmed status per zone | Armed / Disarmed | An armed zone is empty, so any HVAC or lighting running there is waste |

KPIs the dashboard calculates

| KPI | Insight |
| --- | --- |
| Energy per occupant (kWh/person) | Usage efficiency based on real occupancy |
| Energy used in armed / empty zones (kWh) | Clear after-hours waste |
| Actual building hours vs HVAC/lighting schedule | Schedules longer than real use |
| Energy excluded during fire alarms and drills | Cleaner analysis without abnormal periods |

Minimum set if the provider can give only a little: access control occupancy counts (per building or floor) and intrusion armed/disarmed status per zone. These two give the strongest energy insights from this group.

Static data to collect once: the zone mapping between access-control / intrusion zones and the HVAC and lighting zones, so occupancy can be matched to the energy of the same space.

Kept for future safety and security dashboards: detector-level alarms, device faults, sprinkler pressure, fire pump tests, door-forced alarms and camera health.

# Energy Supply and Measurement Systems

# 15. Electrical Distribution and Energy Metering

This is the backbone of the dashboard: almost every KPI is built on it. Meters are arranged in a hierarchy: main incomer → floor / panel meters → system meters (HVAC, lighting, lifts, pumps). Most meters communicate over Modbus. Without sub-meters, only the building total is visible and it's impossible to say where energy goes.

Required

| Data point | Unit | Why it's needed |
| --- | --- | --- |
| Main incomer energy (grid import) | kWh | Total grid consumption |
| Main incomer power | kW | Live building load |
| Maximum demand | kVA or kW | Drives demand charges on the electricity bill |
| Power factor | – | Power factor penalties or incentives |
| Sub-meter energy per floor / panel / major system | kWh | Where energy goes |
| Sub-meter power per floor / panel / major system | kW | Live load per area and system |

Good to have

| Data point | Unit | Adds |
| --- | --- | --- |
| Voltage and current per phase (main incomer) | V, A | Phase imbalance and losses |
| Reactive energy | kVArh | Checks power factor billing |
| Energy exported to grid (if solar exports) | kWh | Net metering |

KPIs the dashboard calculates

| KPI | Formula / insight |
| --- | --- |
| Total consumption (kWh per day / month) | Overall trend |
| EUI (kWh/m² per year) | Compares buildings of different sizes |
| Breakdown by system and floor (%) | Where energy goes |
| Peak demand vs contract demand | Risk of demand penalties |
| Load factor | Average load ÷ peak load; low values mean spiky demand |
| Base load (night / weekend minimum, kW) | Energy used when the building is empty |
| Day / night and weekday / weekend split | After-hours consumption |
| Unaccounted energy | Main incomer − sum of sub-meters; gaps in metering |
| Energy cost (₹ or €) | Energy and demand × tariff |

Minimum set if the provider can give only a little: main incomer energy, power, maximum demand and power factor, plus sub-meters for HVAC, lighting and each floor. That's enough to show total consumption, the system and floor breakdown, peak demand and base load.

Static data to collect once: the electrical single-line diagram, the meter list with location and what each meter measures (parent and child meters), CT ratios, contract demand and the electricity tariff structure (including time-of-day rates).

Kept for future maintenance use: harmonics, voltage dips and swells, breaker trips and transformer temperature.

# 16. Diesel Generator (DG) System

DG sets supply power during grid outages. Diesel power usually costs several times more per kWh than grid power, so DG running time and efficiency matter for cost.

Required

| Data point | Unit | Why it's needed |
| --- | --- | --- |
| Energy generated | kWh | DG share of building energy |
| On/off status and run hours | – / hours | How long DGs run |
| Fuel consumption (or fuel tank level) | litres | Diesel used, for efficiency and cost |
| Load | kW or % | Efficiency is poor at low load |

Good to have

| Data point | Unit | Adds |
| --- | --- | --- |
| Grid / mains failure status | On / Off | Separates power-cut running from tests |
| Number of starts and test runs | count | Test-run energy and fuel |

KPIs the dashboard calculates

| KPI | Formula / insight |
| --- | --- |
| DG energy share of total (%) | Dependence on backup power |
| Specific fuel consumption (kWh per litre) | DG efficiency; higher is better |
| Diesel cost per kWh vs grid cost per kWh | Cost of power cuts |
| Average DG load (%) | Under-loaded DGs waste fuel |
| DG run hours per month | Outage and test patterns |

Minimum set if the provider can give only a little: energy generated, run hours, and fuel consumption or tank level. That's enough to show DG energy, kWh per litre and diesel cost.

Static data to collect once: the DG list with rating (kVA), rated fuel consumption, fuel tank capacity and the diesel price.

Kept for future maintenance use: battery voltage, coolant temperature, oil pressure, alarms and service hours.

# 17. Solar / Renewable Energy System

On-site solar reduces grid consumption. Data usually comes from the inverters or a solar generation meter.

Required

| Data point | Unit | Why it's needed |
| --- | --- | --- |
| Energy generated | kWh | Renewable contribution |
| Instantaneous power | kW | Live generation |
| Inverter status | On / Off / Fault | Explains generation drops |
| Energy exported to grid (if any) | kWh | Net metering |

Good to have

| Data point | Unit | Adds |
| --- | --- | --- |
| Solar irradiance | W/m² | Expected vs actual generation |
| Module temperature | °C | Explains lower output on hot days |
| Generation per inverter | kWh | Finds under-performing inverters |

KPIs the dashboard calculates

| KPI | Formula / insight |
| --- | --- |
| Renewable share of total energy (%) | Sustainability performance |
| Specific yield (kWh per kWp) | Compares plants of different sizes |
| Performance ratio (%) | Actual vs expected generation from irradiance; low values mean dirty panels or faults |
| Grid savings (₹ or €) | Value of solar generation |
| CO₂ avoided (kg) | Generation × grid emission factor |

Minimum set if the provider can give only a little: energy generated and inverter status. That's enough to show solar generation, renewable share and savings.

Static data to collect once: installed capacity (kWp), inverter list, panel tilt and orientation, commissioning date and expected annual generation.

Kept for future maintenance use: string faults, inverter alarms and panel cleaning schedule.

# 18. Gas Supply and Metering System

Gas (piped natural gas or LPG) supplies boilers, kitchens and laundries. Gas is measured in m³ (or SCM) or kg, and must be converted to kWh using the supplier's calorific value so it can be added to electricity for total building energy (natural gas is roughly 10–11 kWh per m³).

Required

| Data point | Unit | Why it's needed |
| --- | --- | --- |
| Gas consumption, main meter | m³, SCM or kg | Total gas used |
| Gas consumption per user (boilers, kitchen, laundry) via sub-meters | m³, SCM or kg | Where gas goes |

Good to have

| Data point | Unit | Adds |
| --- | --- | --- |
| Gas flow rate | m³/h | Live usage and peaks |
| LPG bank / tank level (LPG sites) | % or kg | Consumption where no flow meter exists |

KPIs the dashboard calculates

| KPI | Formula / insight |
| --- | --- |
| Gas energy (kWh) | Gas volume × calorific value |
| Gas share of total energy (%) | Comparison with electricity |
| Gas use by user (%) | Boilers vs kitchen vs laundry |
| Gas consumed outside operating hours | Equipment left on |
| Gas cost (₹ or €) | Volume × tariff |

Minimum set if the provider can give only a little: main gas meter consumption. Add sub-meters per major user when available.

Static data to collect once: gas type (PNG or LPG), calorific value from the supplier bill, the meter list with what each meter feeds, and the gas tariff.

Gas leak alarms and shut-off valve status are covered in Section 14.3.

# Building-type-specific Systems (where present)

# 19. Kitchen Equipment

Large in hotels, hospitals, malls and campuses. Kitchen ventilation is covered in Section 4.2.

Required

| Data point | Unit | Why it's needed |
| --- | --- | --- |
| Kitchen electricity (sub-meter) | kWh | Electrical kitchen consumption |
| Kitchen gas (sub-meter) | m³ or kg | Gas kitchen consumption |
| Meals / covers served (from operations) | count | Energy per meal |
| Kitchen operating hours | time | Energy used outside cooking hours |

Good to have

| Data point | Unit | Adds |
| --- | --- | --- |
| Major equipment on/off status (ovens, fryers, dishwashers) | On / Off | Equipment left on when idle |

KPIs the dashboard calculates

| KPI | Insight |
| --- | --- |
| Energy per meal (kWh per cover) | Kitchen efficiency and benchmarking |
| Kitchen share of total energy (%) | Comparison with other systems |
| Idle energy outside operating hours (kWh) | Equipment left on |

Minimum set if the provider can give only a little: kitchen electricity and gas sub-meters plus meals served.

Static data to collect once: the major equipment list with rated power (kW) and fuel type.

# 20. Laundry Equipment

Large in hotels and hospitals. Uses electricity, steam or gas, and water.

Required

| Data point | Unit | Why it's needed |
| --- | --- | --- |
| Laundry electricity (sub-meter) | kWh | Electrical consumption |
| Steam or gas consumption | kg or m³ | Thermal energy for washing and drying |
| Water consumption | m³ | Water use |
| Linen processed (from operations) | kg | Energy and water per kg |

Good to have

| Data point | Unit | Adds |
| --- | --- | --- |
| Washer and dryer on/off status | On / Off | Machines running part-loaded or idle |

KPIs the dashboard calculates

| KPI | Insight |
| --- | --- |
| Energy per kg of linen (kWh/kg) | Laundry efficiency |
| Water per kg of linen (litres/kg) | Water efficiency |
| Laundry share of total energy (%) | Comparison with other systems |

Minimum set if the provider can give only a little: laundry energy sub-meter, water meter and kg of linen processed.

Static data to collect once: the machine list with capacity (kg) and rated power (kW).

# 21. Swimming Pool and Spa System

Found in hotels, clubs and residential complexes. Energy goes to water heating and filtration pumps.

Required

| Data point | Unit | Why it's needed |
| --- | --- | --- |
| Pool heating energy | kWh or m³ | Heating consumption |
| Filtration pump energy | kWh | Pumping consumption |
| Pool water temperature and setpoint | °C | Overheating waste |
| Pump on/off status and run hours | – / hours | Pumps running outside needed hours |
| Pool operating hours | time | Heating and pumping outside opening hours |

Good to have

| Data point | Unit | Adds |
| --- | --- | --- |
| Pool cover status | On / Off | Covers cut heat loss at night |
| Pump speed (VFD) | % or Hz | Energy savings from slower night filtration |
| Make-up water | m³ | Evaporation and leaks |

KPIs the dashboard calculates

| KPI | Insight |
| --- | --- |
| Pool energy per day (kWh) | Trend and comparison |
| Heating outside opening hours | Direct waste |
| Overheating time (hours above setpoint) | Water heated more than needed |
| Pool share of total energy (%) | Comparison with other systems |

Minimum set if the provider can give only a little: heating energy, pump energy, and water temperature and setpoint.

Static data to collect once: pool and spa volume (m³), heater type and rated capacity (kW), and pump rated power (kW).

# 22. Guest Room Management System (GRMS, hotels)

Uses almost no energy itself, but gives the room-level occupancy that hotel energy KPIs depend on. Room sold status comes from the hotel PMS.

Required

| Data point | Unit | Why it's needed |
| --- | --- | --- |
| Room occupancy (key card / presence) | Occupied / vacant | Guest in the room or out |
| Room sold status (from PMS) | Sold / unsold | AC and lights in unsold rooms are waste |
| Room AC on/off, setpoint and room temperature | On / Off, °C | Setback when the guest is out |
| Room lighting on/off | On / Off | Lights left on in empty rooms |

Good to have

| Data point | Unit | Adds |
| --- | --- | --- |
| Window / balcony door open status | Open / Closed | AC running with the window open |

KPIs the dashboard calculates

| KPI | Insight |
| --- | --- |
| Energy per occupied room (kWh per room sold) | The main hotel energy KPI; fair comparison across hotels |
| AC running in unsold rooms (rooms, kWh) | Direct waste |
| Setback compliance (%) | Rooms correctly set back when the guest is out |
| AC on with window open (hours) | Avoidable cooling loss |

Minimum set if the provider can give only a little: room occupancy, room sold status, and room AC status and setpoint.

Static data to collect once: the room list with floor, room type, area (m²) and the FCU serving each room.

# Part 3: Context Data and Common Data Rules

## Context data (from outside the BMS)

Consumption only becomes insight when it's compared with something. This data comes from the building owner, operations or external sources, not from the BMS.

| Data | Purpose |
| --- | --- |
| Building area per building / floor (m²) | EUI and fair comparisons |
| Operating hours and holidays | After-hours waste detection |
| Occupancy (headcount, PMS, access control) | Energy per occupant or per occupied room |
| Outdoor temperature and humidity (BMS sensor or weather service) | Weather normalisation |
| Tariffs (electricity incl. time-of-day and demand charges, gas, diesel, water) | Cost calculations |
| Historical consumption (at least 12 months) | Baseline for savings |
| Savings targets | Progress tracking against goals |

## Common rules for all data

- Polling interval: every 10–30 minutes, the same interval across all systems where possible.

- Energy meters: send the cumulative kWh register reading, not only instantaneous kW, so no energy is lost between readings.

- Timestamps: every reading carries a timestamp with its time zone (e.g. IST, UTC+05:30).

- Units: every data point has a defined unit, as listed in this document.

- Naming: one consistent naming / tagging convention for all points (e.g. Building → Floor → Zone → Equipment → Data point).

- Data quality: missing or faulty readings are flagged, not filled with zero, so gaps don't look like low consumption.

- Access: the energy platform has read-only access to the BMS; it never sends commands.

- Maintenance data: not required now; the "Kept for future maintenance use" lists define the next phase.