BEACON

Database design for BMS energy data

This document describes how the BMS data for the energy efficiency dashboard is organised and stored: which tables there are, what each one holds, how they connect, and how the data moves from a building's controllers to the dashboard and the PDF reports.

It is a design on paper. Nothing has been built yet. It is based on the BMS data requirements document (BEACON: BMS data requirements) and the demo dashboard, and uses the same systems, names and KPIs.

| Item | Detail |
| --- | --- |
| Document | Database design for BMS energy data |
| Version | 1.0 (design) |
| Date | 10 October 2026 |
| Status | Design only, not implemented |
| Related documents | BMS data requirements for the energy efficiency dashboard; BEACON demo dashboard |
| Recommended database | PostgreSQL 16 with the TimescaleDB extension |

# Contents

Right-click the table of contents in Word and choose Update Field if page numbers are missing.

# 1. Purpose and scope

The energy hypervision collects readings from the BMS of many buildings every 15 minutes, turns them into energy, cost, KPIs and waste findings, and shows them on a live dashboard and in reports. The database must:

- store every reading from every building, with its time, unit and quality, without losing any data during network outages;

- know what each reading is: which building, floor, zone, system and equipment it belongs to;

- keep calculated results (energy by system, cost, KPIs, waste) so the dashboard is fast and reports match the screen;

- record faults, alarms and data gaps;

- control who can see which building;

- grow from a few buildings to many without a redesign.

In scope: energy efficiency data, as listed in the data requirements document. Out of scope for now: the maintenance data marked "Kept for future maintenance use". The design leaves room for it: maintenance points can be added as new data points later without changing any table.

## Why PostgreSQL with TimescaleDB

| Need | How it is met |
| --- | --- |
| Very many time-stamped readings | TimescaleDB stores them in time-based chunks and compresses old chunks (typically by 90% or more), so the database stays small and fast |
| Master data with relationships (building, floor, equipment) | Standard PostgreSQL tables with foreign keys keep the asset register consistent |
| Hourly and daily summaries | Continuous aggregates keep them up to date automatically |
| One database for both | Readings can be joined directly with buildings, equipment and tariffs in one query |
| Cost and support | Both are open source and widely supported; managed cloud versions exist |

# 2. Design principles

- One reading = one data point + one time + one value. All systems use the same reading table. Adding a new system or sensor means adding rows to the data point list, not new tables.

- Master data is separate from readings. What a sensor is (building, equipment, unit) is stored once in the asset register. Readings carry only a small point number.

- Raw readings are never changed or deleted during their retention period. Corrections and estimates are stored as calculated values, so the original can always be checked.

- Calculated results are stored, with their source marked (metered, estimated or calculated), so everyone sees the same numbers.

- Times are stored in UTC and shown in each building's local time. Every reading keeps the time it was measured, not the time it arrived.

- Every value has one fixed unit. Units are converted at ingest, never in the dashboard.

- Missing is not zero. Gaps and bad values are flagged, never filled with 0.

- Read-only from the BMS. The platform never writes back to the BMS.

- Access is enforced in the database, by building, so a building manager can only ever read their own building.

# 3. How the data is organised

## 3.1 The building hierarchy

Every reading is filed under a fixed chain, from the portfolio down to the single value:

| Level | Example | Stored in |
| --- | --- | --- |
| Portfolio (owner) | Your company | core.organization |
| Building | GRH: Grand Residency Hotel, Chennai | core.building |
| Floor | Level 3 | core.floor |
| Zone / room | Room 1204, Floor 3 east wing, Car park B1 | core.zone |
| System | AHU: Air Handling Units | core.system_type |
| Equipment | AHU03 (ballroom AHU), part of the air-side system | core.equipment |
| Data point | GRH-AHU-AHU03-KW: fan power in kW | core.data_point |
| Reading | 10 Oct 2026 14:15, 18.4 kW, quality good | ts.reading |

Meters sit beside this chain: a meter measures a plant, a panel or a whole building, and its readings are data points like any other. The meter tree (main incomer and sub-meters) is held in core.meter.

## 3.2 How data flows into the database

Figure 1. From the BMS controllers to the dashboard

- The edge gateway in each building reads the BMS controllers and meters every 15 minutes (BACnet or Modbus), and stores readings locally if the internet link is down.

- It sends them to the central ingest service (MQTT or HTTPS). The ingest service looks up each tag in core.data_point, converts units, checks ranges and saves the readings in ts.reading with a quality flag.

- Calculation jobs run every 15 minutes, hourly and daily. They combine readings with tariffs, schedules, occupancy and weather, and write energy, cost, KPIs and waste findings to the energy tables, and data gaps and platform alarms to the ops tables.

- The dashboard and reports read only the calculated tables, plus ts summaries for detailed charts.

## 3.3 Six groups of tables

The tables are grouped into six PostgreSQL schemas (folders). Each group has a different job and changes at a different pace.

| Schema | Holds | Changes | Main tables |
| --- | --- | --- | --- |
| core | Asset register: buildings, floors, zones, systems, equipment, meters, data points, gateways | Rarely (commissioning, new equipment) | building, equipment, meter, data_point |
| ts | Raw readings and their hourly / daily summaries | Every 15 minutes, very large | reading, ingest_batch |
| energy | Calculated energy, cost, KPIs, targets, waste findings | Every 15 minutes | energy_interval, energy_daily, kpi_value, waste_finding |
| ops | Alarms and faults, gateway health, data gaps | When events happen | alarm_event, gateway_status, data_gap |
| ctx | Context from outside the BMS: tariffs, schedules, holidays, occupancy, weather, baseline | Monthly or hourly | tariff, schedule, occupancy, weather |
| app | Users, roles, building access, report log, audit log | When users act | app_user, user_building_access, report_log |

## 3.4 How the main tables connect

Figure 2. Main tables and relationships (the forked end means "many": one building has many floors)

core.data_point is the link between the asset register and the readings. ts.reading has only four columns, so billions of rows stay compact; everything else about a reading is found by following point_id.

# 4. Naming convention for data points

Every data point gets one standard tag, whatever the BMS calls it. The BMS name is kept in data_point.bms_name for traceability. The standard tag makes points readable, sortable and the same across all buildings.

## 4.1 Tag format

BUILDING - SYSTEM - EQUIPMENT - POINT

| Tag | Means |
| --- | --- |
| TPA-CHL-CH01-KW | Tech Park Tower A, chiller plant, chiller 1, power (kW) |
| TPA-CHL-PLANT-TRH | Tech Park Tower A, chiller plant, BTU meter, cooling energy (TRh) |
| GRH-AHU-AHU03-SAT | Grand Residency Hotel, AHU 3, supply air temperature |
| GRH-FCU-R1204-ZTSP | Grand Residency Hotel, fan coil unit in room 1204, room setpoint |
| CSM-VEN-JF07-ST | City Square Mall, car park jet fan 7, run status |
| CSM-ELE-MAIN-KWH | City Square Mall, main incomer energy register |

Building codes are 3 letters, unique in the portfolio. Equipment tags have no spaces or hyphens (CH01, AHU03, R1204, F3E). PLANT, MAIN or GROUP are used when the point belongs to a whole plant, a main meter or a group of items.

## 4.2 System codes

One code per system from the data requirements document. Loaded once into core.system_type.

| Code | System | Category |
| --- | --- | --- |
| CHL | Chiller Plant | Consumer |
| AHU | Air Handling Units / TFA | Consumer |
| FCU | Fan Coil Units | Consumer |
| LTG | Lighting Control (indoor and external) | Consumer |
| VEN | Ventilation and Exhaust | Consumer |
| VTR | Elevators and Escalators | Consumer |
| BLR | Boiler / Heating / Heat Pumps | Consumer |
| HWS | Hot Water System | Consumer |
| WSP | Water Supply (pumping) | Consumer |
| CLD | Cold Room / Refrigeration | Consumer |
| UPS | UPS System | Consumer |
| STP | Sewage Treatment Plant | Consumer |
| WTP | Water Treatment Plant | Consumer |
| IAQ | Indoor Air Quality Monitoring | Context |
| FAS | Fire Alarm | Life safety (context) |
| SMK | Smoke Control | Life safety (context) |
| GLD | Gas Leak Detection | Life safety (context) |
| ACS | Access Control | Security (context) |
| CCT | CCTV | Security (context) |
| IDS | Intrusion Alarm | Security (context) |
| ELE | Electrical Distribution and Energy Metering | Supply / metering |
| DGS | Diesel Generator | Supply / metering |
| SOL | Solar / Renewable Energy | Supply / metering |
| GAS | Gas Supply and Metering | Supply / metering |
| KIT | Kitchen Equipment | Building-type specific |
| LDY | Laundry Equipment | Building-type specific |
| POL | Swimming Pool and Spa | Building-type specific |
| GRM | Guest Room Management (GRMS) | Building-type specific |

## 4.3 Point codes

The last part of the tag says what is measured. The list grows as needed; the most common are:

| Code | Measures | Unit |
| --- | --- | --- |
| KW | Power | kW |
| KWH | Energy register (cumulative) | kWh |
| KVA | Apparent power | kVA |
| PF | Power factor | - |
| ST | Run status | 0 = off, 1 = on |
| RH | Run hours (counter) | hours |
| ALM | Alarm / trip | 0 / 1 |
| MODE | Operating mode | multistate |
| SPD | Fan / pump speed | % |
| SAT / SATSP | Supply air temperature / setpoint | °C |
| RAT | Return air temperature | °C |
| CHWS / CHWR | Chilled water supply / return temperature | °C |
| CHWSP | Chilled water setpoint | °C |
| FLOW | Water flow | m³/h |
| TR / TRH | Cooling load / cooling energy (BTU meter) | TR / TRh |
| ZT / ZTSP | Zone (room) temperature / setpoint | °C |
| RHUM | Relative humidity | %RH |
| CO2 / CO | Carbon dioxide / carbon monoxide | ppm |
| OCC | Occupancy | 0 / 1 |
| LUX | Light level | lux |
| DIM | Dimming level | % |
| TRIPS | Elevator trips (counter) | count |
| VOL | Water / gas / diesel volume (counter) | m³ or litres |

# 5. Table definitions

Column types are PostgreSQL types. Key: PK = primary key, FK = foreign key (link to another table), UQ = unique. Columns marked created_at / updated_at exist on all master data tables for change tracking.

## 5.1 core: asset register

### core.organization

The company that owns the buildings. One row in most installations; kept so the platform can serve more than one owner later.

| Column | Type | Key | Description |
| --- | --- | --- | --- |
| org_id | integer | PK | Identifier |
| name | text |  | Company name, as printed on reports |
| logo | bytea |  | Company logo (PNG) for reports |
| default_timezone | text |  | e.g. Asia/Kolkata |

### core.building

One row per building (site). Everything else hangs off this table.

| Column | Type | Key | Description |
| --- | --- | --- | --- |
| building_id | integer | PK | Identifier |
| org_id | integer | FK | Owner, core.organization |
| code | varchar(6) | UQ | Short code used in tags, e.g. TPA, GRH, CSM |
| name | text |  | e.g. Grand Residency Hotel |
| building_type | text |  | Office, Hotel, Mall, Hospital, ... |
| city, address | text |  | Location |
| timezone | text |  | Local time zone for schedules and reports |
| gross_area_m2 | numeric(10,1) |  | Floor area, used for EUI and kWh/m² |
| conditioned_area_m2 | numeric(10,1) |  | Air-conditioned area (optional) |
| room_count | integer |  | Hotels: number of keys, for kWh per occupied room |
| contract_demand_kva | numeric(8,1) |  | Sanctioned demand, for peak demand alerts |
| is_active | boolean |  | Building included in the portfolio |
| created_at | timestamptz |  | When the row was created |
| updated_at | timestamptz |  | When the row last changed |

### core.floor

Floors (levels) of a building, including basements and roof.

| Column | Type | Key | Description |
| --- | --- | --- | --- |
| floor_id | integer | PK | Identifier |
| building_id | integer | FK | core.building |
| level | smallint |  | -2 = basement 2, 0 = ground, 1, 2, ... |
| name | text |  | e.g. B2, Ground, Roof |
| area_m2 | numeric(10,1) |  | Floor area |

### core.zone

Areas inside a floor that are controlled or metered together: a room, an office wing, a corridor, a car park, a plant room.

| Column | Type | Key | Description |
| --- | --- | --- | --- |
| zone_id | integer | PK | Identifier |
| floor_id | integer | FK | core.floor |
| code | varchar(20) |  | e.g. F3-EAST, R1204, CP-B1 |
| zone_type | text |  | Guest room, Office, Corridor, Lobby, Car park, Kitchen, Plant room, ... |
| area_m2 | numeric(10,1) |  | Zone area, used for lighting power density |
| lighting_load_kw | numeric(8,2) |  | Connected lighting load (static data) |

### core.system_type

The fixed list of BMS systems from the data requirements document (see Section 4.2). Loaded once.

| Column | Type | Key | Description |
| --- | --- | --- | --- |
| system_code | varchar(4) | PK | e.g. CHL, AHU, LTG |
| name | text |  | e.g. Chiller Plant |
| category | text |  | Consumer, Supply / metering, Building-type specific, Context (IAQ, safety) |
| energy_rank | smallint |  | Rank by typical energy use (1 = chiller plant) |
| dashboard_group | text |  | Band in the stacked load chart (Chiller, AHU / FCU, Lighting, ...) |

### core.equipment

Every physical item the BMS knows about: chillers, pumps, AHUs, FCUs, lighting circuits, lifts, meters' parent panels, and so on. Equipment can belong to other equipment, e.g. a pump belongs to the chiller plant.

| Column | Type | Key | Description |
| --- | --- | --- | --- |
| equipment_id | integer | PK | Identifier |
| building_id | integer | FK | core.building |
| zone_id | integer | FK | Where it is, or which zone it serves (optional) |
| system_code | varchar(4) | FK | core.system_type |
| parent_equipment_id | integer | FK | Plant or group it belongs to (self reference) |
| tag | varchar(20) | UQ* | e.g. CH01, CHWP02, AHU03 (*unique per building) |
| name | text |  | e.g. Chiller 1 (water-cooled, 300 TR) |
| equipment_type | text |  | Chiller, Pump, Cooling tower, AHU, FCU, Lighting circuit, Elevator, ... |
| rated_power_kw | numeric(8,2) |  | Nameplate power; used to estimate energy where there is no meter |
| rated_capacity | numeric(10,2) |  | e.g. 300 |
| capacity_unit | text |  | TR, kW, m³/h, kVA, passengers, ... |
| design_efficiency | numeric(6,3) |  | e.g. design kW/TR, UPS efficiency |
| manufacturer, model | text |  | Make and model |
| installed_on | date |  | Installation date |
| is_active | boolean |  | Still in service |
| created_at | timestamptz |  | When the row was created |
| updated_at | timestamptz |  | When the row last changed |

### core.meter

Energy and utility meters, arranged as a tree: main incomer at the top, sub-meters below. The tree lets the system check that sub-meters add up to the main meter and shows unmetered ("other") energy.

| Column | Type | Key | Description |
| --- | --- | --- | --- |
| meter_id | integer | PK | Identifier |
| building_id | integer | FK | core.building |
| parent_meter_id | integer | FK | Upstream meter (self reference); empty for a main incomer |
| code | varchar(20) |  | e.g. EM-MAIN, EM-CHL, BTU-01 |
| meter_type | text |  | Electricity, BTU (thermal), Gas, Diesel, Water, Solar generation |
| serves_equipment_id | integer | FK | Equipment or plant the meter measures (optional) |
| serves_system_code | varchar(4) | FK | System the meter's energy belongs to |
| multiplier | numeric(10,4) |  | CT / PT ratio applied to raw values |
| is_virtual | boolean |  | Calculated meter (e.g. main minus sub-meters) |

### core.data_point

The heart of the design. Every value the BMS sends (a temperature, a kW, an on/off status, a meter register) is one data point with a fixed unit. Every reading points to exactly one data point.

| Column | Type | Key | Description |
| --- | --- | --- | --- |
| point_id | integer | PK | Identifier (small integer keeps the reading table compact) |
| point_code | varchar(60) | UQ | Standard tag, e.g. TPA-CHL-CH01-KW (see Section 4) |
| building_id | integer | FK | core.building |
| equipment_id | integer | FK | Equipment the point belongs to |
| meter_id | integer | FK | Set when the point is a meter value |
| gateway_id | integer | FK | Gateway that reads it |
| bms_address | text |  | Source address: BACnet device + object, or Modbus register |
| bms_name | text |  | Name used in the BMS, kept for traceability |
| quantity | text |  | Power, Energy, Temperature, Flow, Status, Speed, CO₂, ... |
| unit_code | varchar(12) | FK | core.unit, e.g. kW, kWh, degC |
| value_type | text |  | Analog, Binary, Multistate, Counter (cumulative register) |
| state_map | jsonb |  | Meaning of binary / multistate values, e.g. {0: Off, 1: On} |
| requirement | text |  | Required, Good to have, Maintenance (future), as in the data requirements |
| valid_min, valid_max | double precision |  | Plausible range; values outside are flagged |
| interval_min | smallint |  | Expected reading interval (15) |
| is_active | boolean |  | Point still being read |
| created_at | timestamptz |  | When the row was created |
| updated_at | timestamptz |  | When the row last changed |

### core.unit

The list of allowed units, so every value has a defined unit.

| Column | Type | Key | Description |
| --- | --- | --- | --- |
| unit_code | varchar(12) | PK | kW, kWh, kVA, degC, pct, m3h, TR, TRh, ppm, lux, Pa, hours, count, ... |
| name | text |  | Full name |
| quantity | text |  | What it measures |

### core.gateway

The edge gateway (industrial PC) in each building that reads the BMS and sends data to the central database.

| Column | Type | Key | Description |
| --- | --- | --- | --- |
| gateway_id | integer | PK | Identifier |
| building_id | integer | FK | core.building |
| code | varchar(20) | UQ | e.g. GW-TPA-01 |
| protocols | text |  | BACnet/IP, Modbus TCP, ... |
| firmware_version | text |  | Software version on the gateway |
| buffer_capacity_days | smallint |  | How long it can store readings while offline |

## 5.2 ts: readings

### ts.reading

Every reading received, at its original 15-minute timestamp. This is the only table that grows fast. It is a TimescaleDB hypertable, split into one chunk per week and compressed after 7 days.

| Column | Type | Key | Description |
| --- | --- | --- | --- |
| point_id | integer | PK, FK | core.data_point |
| ts | timestamptz | PK | Time of the reading at the source (stored in UTC, shown in local time) |
| value | double precision |  | The reading. Status values stored as numbers (0 = off, 1 = on), meaning in data_point.state_map |
| quality | smallint |  | 0 = good, 1 = estimated, 2 = suspect, 3 = bad (see Section 7) |
| batch_id | bigint | FK | ts.ingest_batch the value arrived in |

Primary key (point_id, ts) means a reading sent twice is stored once, so a gateway can safely resend its buffer.

### ts.ingest_batch

One row per message received from a gateway. Shows when data arrived and whether it was live or buffered (late) data.

| Column | Type | Key | Description |
| --- | --- | --- | --- |
| batch_id | bigint | PK | Identifier |
| gateway_id | integer | FK | core.gateway |
| received_at | timestamptz |  | When the central system received it |
| first_ts, last_ts | timestamptz |  | Time range of the readings inside |
| record_count | integer |  | Number of readings |
| rejected_count | integer |  | Readings rejected (unknown tag, bad format) |
| is_backfill | boolean |  | True when the gateway is sending buffered readings after an outage |

### ts.reading_hourly and ts.reading_daily

Summaries kept up to date automatically (TimescaleDB continuous aggregates). Charts over weeks or months read these, not the raw table.

| Column | Type | Key | Description |
| --- | --- | --- | --- |
| point_id | integer | PK | core.data_point |
| bucket | timestamptz | PK | Start of the hour or day |
| avg_value, min_value, max_value | double precision |  | For analog points |
| last_value | double precision |  | Last reading in the bucket (meter registers) |
| delta_value | double precision |  | Last minus first: energy used in the bucket for counters |
| on_minutes | integer |  | Minutes in On state, for status points (run hours) |
| samples, good_samples | smallint |  | Readings received and readings of good quality |

## 5.3 energy: calculated results

### energy.energy_interval

Energy per building, per system, per 15 minutes. The main table behind the dashboard's load profile, energy by system and cost. Filled by a calculation job from meter readings; where a system has no meter, the energy is estimated and marked.

| Column | Type | Key | Description |
| --- | --- | --- | --- |
| building_id | integer | PK, FK | core.building |
| system_code | varchar(4) | PK, FK | core.system_type |
| ts | timestamptz | PK | Start of the 15-minute interval |
| kwh | numeric(12,3) |  | Energy in the interval |
| kw_avg | numeric(10,2) |  | Average power |
| source | text |  | Metered, Estimated (rated power × run time), Calculated (main minus sub-meters) |
| supply_mix | jsonb |  | kWh from grid, DG and solar |
| cost | numeric(12,2) |  | Cost in rupees at the tariff band of that interval |
| tariff_band | text |  | Normal, Peak, Off-peak |
| waste_kwh | numeric(12,3) |  | Part of the energy flagged as avoidable |

### energy.energy_daily

One row per building per day. Feeds daily totals, comparisons, reports and the data completeness figure.

| Column | Type | Key | Description |
| --- | --- | --- | --- |
| building_id, day | integer, date | PK | Building and local date |
| kwh_total, kwh_grid, kwh_dg, kwh_solar | numeric(12,1) |  | Energy by source |
| cost_total | numeric(12,2) |  | Energy cost |
| peak_kva, peak_kva_at | numeric, timestamptz |  | Highest 15-minute demand and when |
| cooling_trh | numeric(12,1) |  | Cooling delivered (for kW/TR) |
| avg_outdoor_temp | numeric(4,1) |  | For weather-normalised comparison |
| occupancy | numeric(8,1) |  | Occupied rooms or headcount |
| readings_received, readings_expected | integer |  | Data completeness |

### energy.kpi_definition

The list of KPIs and how each is calculated, taken from the "KPIs the dashboard calculates" tables in the data requirements document.

| Column | Type | Key | Description |
| --- | --- | --- | --- |
| kpi_code | varchar(30) | PK | e.g. CHL_PLANT_KW_PER_TR |
| name | text |  | e.g. Chiller plant efficiency |
| system_code | varchar(4) | FK | System it belongs to |
| unit_code | varchar(12) | FK | e.g. kW/TR |
| formula | text |  | Plain-language formula, e.g. plant kWh ÷ TRh |
| better | text |  | Lower or Higher |
| periods | text[] |  | 15min, Hour, Day, Month |

### energy.kpi_target

Targets and alert limits. A building-specific row overrides the portfolio default; rows are dated so past results keep the target that applied at the time.

| Column | Type | Key | Description |
| --- | --- | --- | --- |
| target_id | integer | PK | Identifier |
| kpi_code | varchar(30) | FK | energy.kpi_definition |
| building_id | integer | FK | Empty = default for all buildings |
| target_value | numeric |  | e.g. 0.65 |
| warning_value, critical_value | numeric |  | Limits for amber and red status |
| valid_from, valid_to | date |  | Period the target applies |

### energy.kpi_value

Calculated KPI results. Storing them (instead of recalculating on every page load) keeps the dashboard fast and means reports show the same numbers as the screen.

| Column | Type | Key | Description |
| --- | --- | --- | --- |
| kpi_code | varchar(30) | PK, FK | energy.kpi_definition |
| building_id | integer | PK, FK | core.building |
| equipment_id | integer | PK, FK | Set for equipment-level KPIs (0 = whole building or system) |
| period_type | text | PK | 15min, Hour, Day, Month |
| period_start | timestamptz | PK | Start of the period |
| value | numeric |  | Result |
| target_value | numeric |  | Target that applied |
| status | text |  | Good, Warning, Critical, No data |

### energy.waste_rule

The checks that find waste, e.g. "chiller running outside schedule" or "lights on in an empty zone".

| Column | Type | Key | Description |
| --- | --- | --- | --- |
| rule_id | integer | PK | Identifier |
| code | varchar(40) | UQ | e.g. CHL_AFTER_HOURS |
| system_code | varchar(4) | FK | System checked |
| description | text |  | What the rule looks for |
| default_action | text |  | Recommended fix shown to the user |
| severity | text |  | Warning or Critical |

### energy.waste_finding

Each problem found, from first detection until it is fixed. This is the "Savings opportunities" list on the dashboard and in the reports.

| Column | Type | Key | Description |
| --- | --- | --- | --- |
| finding_id | bigint | PK | Identifier |
| rule_id | integer | FK | energy.waste_rule |
| building_id, equipment_id | integer | FK | Where it was found |
| first_detected, last_detected | timestamptz |  | When it started and was last seen |
| kwh_per_day, cost_per_month_est | numeric |  | Size of the waste |
| detail | text |  | Evidence, e.g. "Plant at 0.84 kW/TR against 0.65" |
| status | text |  | Open, In progress, Fixed, Dismissed |
| owner_user_id | integer | FK | Person responsible (app.app_user) |
| closed_at, closed_note | timestamptz, text |  | How it was resolved; used to confirm savings |

## 5.4 ops: alarms, gateways and gaps

### ops.alarm_event

Faults and alarms: equipment trips, gateway offline, grid outage and DG running, stuck sensors. Includes alarms that come from the BMS and those raised by the platform's own checks.

| Column | Type | Key | Description |
| --- | --- | --- | --- |
| event_id | bigint | PK | Identifier |
| building_id | integer | FK | core.building |
| equipment_id, point_id | integer | FK | Source of the alarm (optional) |
| system_code | varchar(4) | FK | System affected |
| category | text |  | Equipment, Communication, Power, Data quality |
| severity | text |  | Info, Warning, Critical |
| title, detail, action | text |  | What happened and what to do |
| raw_text | text |  | Original BMS alarm text, e.g. AHU-03 TRIP DI=1 |
| source | text |  | BMS or Platform |
| start_ts, end_ts | timestamptz |  | Start and return to normal |
| status | text |  | Open, Acknowledged, Resolved |
| ack_by, ack_at, ack_note | integer, timestamptz, text |  | Who acknowledged it and when |

### ops.gateway_status

Heartbeat from each gateway (every 5 minutes). Drives the online/offline indicator.

| Column | Type | Key | Description |
| --- | --- | --- | --- |
| gateway_id, ts | integer, timestamptz | PK | Gateway and time |
| online | boolean |  | Gateway reachable |
| buffered_records | integer |  | Readings waiting to be sent |
| cpu_pct, disk_free_pct | numeric(5,1) |  | Basic health of the industrial PC |

### ops.data_gap

Periods with missing readings, so gaps are visible and never read as zero consumption.

| Column | Type | Key | Description |
| --- | --- | --- | --- |
| gap_id | bigint | PK | Identifier |
| gateway_id or point_id | integer | FK | Whole gateway or a single point |
| gap_start, gap_end | timestamptz |  | Missing period |
| reason | text |  | Gateway offline, Point not responding, Value stuck, Out of range |
| filled_by_backfill | boolean |  | True when buffered readings later filled the gap |

## 5.5 ctx: context data

### ctx.tariff and ctx.tariff_band

Prices for electricity (time-of-day), demand charges, diesel, gas and water, dated so that past costs stay correct when tariffs change.

| Column | Type | Key | Description |
| --- | --- | --- | --- |
| tariff_id | integer | PK | Identifier |
| building_id | integer | FK | Building the tariff applies to |
| energy_type | text |  | Electricity, Diesel, Gas, Water |
| valid_from, valid_to | date |  | Period |
| demand_charge_per_kva | numeric(8,2) |  | Monthly demand charge |
| band (tariff_band) | text |  | Normal, Peak, Off-peak |
| start_time, end_time, days | time, time, text |  | When the band applies, e.g. 18:00 to 22:00, all days |
| rate | numeric(8,3) |  | Price per unit (₹/kWh, ₹/litre, ...) |

### ctx.schedule and ctx.holiday

Operating hours per building, zone or system, plus holidays. Used to detect equipment running after hours.

| Column | Type | Key | Description |
| --- | --- | --- | --- |
| schedule_id | integer | PK | Identifier |
| building_id, zone_id, system_code | integer, integer, varchar | FK | What the schedule applies to |
| day_of_week | smallint |  | 1 = Monday ... 7 = Sunday |
| start_time, end_time | time |  | Occupied hours |
| holiday_date, name | date, text |  | Holiday table: days treated as closed |

### ctx.occupancy

Occupancy from the hotel PMS / GRMS, access control or people counters.

| Column | Type | Key | Description |
| --- | --- | --- | --- |
| building_id, zone_id, ts | integer, integer, timestamptz | PK | Where and when |
| occupied_rooms | integer |  | Hotels |
| headcount | integer |  | Offices, malls (footfall) |
| source | text |  | PMS, GRMS, Access control, Counter |

### ctx.weather

Outdoor conditions per building, from the BMS outdoor sensor or a weather service.

| Column | Type | Key | Description |
| --- | --- | --- | --- |
| building_id, ts | integer, timestamptz | PK | Where and when |
| temp_c, rh_pct | numeric(4,1) |  | Temperature and humidity |
| source | text |  | BMS sensor or Weather service |

### ctx.baseline and ctx.savings_target

The reference to measure savings against: at least 12 months of past consumption, and the savings goal.

| Column | Type | Key | Description |
| --- | --- | --- | --- |
| building_id, system_code, month | integer, varchar, date | PK | Scope and month |
| baseline_kwh | numeric(14,1) |  | Consumption in the reference year |
| target_pct | numeric(5,2) |  | Savings goal, e.g. 10% below baseline |

## 5.6 app: users, access and reports

### app.app_user and app.role

People who use the dashboard, and their role.

| Column | Type | Key | Description |
| --- | --- | --- | --- |
| user_id | integer | PK | Identifier |
| name, email | text |  | Name and login (or company single sign-on ID) |
| role_code | text | FK | PORTFOLIO_MANAGER, BUILDING_MANAGER, OPERATOR, ADMIN |
| is_active, last_login_at | boolean, timestamptz |  | Account status |

Passwords are not stored in this database when company single sign-on is used; otherwise only a salted hash is stored.

### app.user_building_access

Which buildings each user may see. The database itself enforces this (row-level security), not only the website.

| Column | Type | Key | Description |
| --- | --- | --- | --- |
| user_id, building_id | integer | PK, FK | One row per user per building |

### app.report_log

Every PDF report generated, so a report number can be traced back to who made it and with which settings.

| Column | Type | Key | Description |
| --- | --- | --- | --- |
| report_no | varchar(30) | PK | e.g. BCN-20261010-0115-PF |
| report_type | text |  | Portfolio, Building, System, Comparison |
| scope | jsonb |  | Buildings, system and sections chosen |
| period_start, period_end | timestamptz |  | Period covered |
| generated_by, generated_at | integer, timestamptz |  | Who and when |
| file_sha256 | text |  | Fingerprint of the PDF, to prove a copy is unchanged |

### app.audit_log

Record of changes to master data, targets, tariffs and alarm acknowledgements.

| Column | Type | Key | Description |
| --- | --- | --- | --- |
| audit_id | bigint | PK | Identifier |
| ts, user_id | timestamptz, integer |  | When and who |
| action | text |  | Create, Update, Delete, Acknowledge, Login, Export |
| table_name, row_key | text |  | What was changed |
| old_value, new_value | jsonb |  | Before and after |

# 6. Worked example: chiller plant efficiency

How one KPI travels through the tables, using the Tech Park Tower A chiller plant (the plant the demo flags for low efficiency).

| Step | Table | What is stored |
| --- | --- | --- |
| 1. Readings arrive | ts.reading | Every 15 min: TPA-ELE-CHLPLANT-KWH (plant energy register, e.g. 4,812,350.2 kWh) and TPA-CHL-PLANT-TRH (BTU meter, e.g. 6,120,880.5 TRh), plus CH01-ST, CHWS, CHWR, FLOW |
| 2. Energy per interval | energy.energy_interval | Register difference: 162.4 kWh in 14:00 to 14:15 for system CHL; cost ₹1,461.60 at the normal band (₹9.00/kWh) |
| 3. Cooling per interval | ts.reading | BTU meter register difference: 193.3 TRh in the same interval (daily total kept in energy_daily.cooling_trh) |
| 4. KPI | energy.kpi_value | CHL_PLANT_KW_PER_TR = 162.4 ÷ 193.3 = 0.84 kW/TR; target 0.65 from kpi_target; status Critical |
| 5. Waste | energy.waste_finding | Rule CHL_LOW_EFFICIENCY opens a finding: 0.84 against 0.65, chilled water ΔT 3.4 °C, estimated ₹2.5 L per month; action: rebalance valves, reset pump setpoint |
| 6. Shown | Dashboard and PDF report | System Detail card, Energy Insights list and the report's Savings opportunities table all read the same rows |

Figures are illustrative, in the style of the demo's simulated data.

## Example KPI definitions

| kpi_code | KPI | Formula | Better |
| --- | --- | --- | --- |
| CHL_PLANT_KW_PER_TR | Chiller plant efficiency | Plant kWh ÷ TRh | Lower |
| CHL_DELTA_T | Chilled water ΔT | Average CHWR − CHWS while running | Higher |
| AHU_AFTER_HOURS_KWH | AHU after-hours energy | AHU kWh outside schedule | Lower |
| LTG_LPD | Lighting power density | Lighting kW × 1000 ÷ zone area | Lower |
| LTG_VACANT_KWH | Lights on in vacant zones | Lighting kWh while OCC = 0 | Lower |
| UPS_EFFICIENCY | UPS efficiency | Output kW ÷ input kW | Higher |
| BLD_EUI | Energy use intensity | Annual kWh ÷ gross area | Lower |
| BLD_KWH_PER_ROOM | Energy per occupied room | Daily kWh ÷ occupied rooms | Lower |
| BLD_PEAK_KVA | Peak demand | Highest 15-minute kVA | Lower |
| BLD_DATA_COMPLETENESS | Data completeness | Readings received ÷ expected | Higher |

# 7. Data quality and late data

## 7.1 Quality flag on every reading

| Code | Meaning | Set when | Used in calculations |
| --- | --- | --- | --- |
| 0 | Good | Value received and passes all checks | Yes |
| 1 | Estimated | Value filled in by the platform (e.g. interpolated for a short gap of one reading) | Yes, marked as estimated |
| 2 | Suspect | Outside the plausible range, a sudden jump, or unchanged for too long (stuck sensor) | No; raises a Data quality alarm |
| 3 | Bad | BMS reports a fault, or the value cannot be read | No |

## 7.2 Rules

- Unknown tags are not saved as readings; they are counted in ingest_batch.rejected_count and listed for the commissioning team to map.

- Meter registers (cumulative kWh) are the source of energy. If a reading is missing, the next register value still gives the correct total over the gap.

- Register resets (meter replaced or rolled over) are detected when the register goes down, and the interval is marked so energy is not counted as negative.

- Stuck values: an analog point that reports the same value for longer than its limit (e.g. CO₂ fixed at 412 ppm for 31 hours) is flagged Suspect and opens a Data quality alarm.

- Late data: when a gateway reconnects, its buffered readings are saved with their original times (is_backfill = true). The calculation jobs then recalculate the affected intervals, so the dashboard fills in the gap, exactly as the demo shows.

- Completeness = readings received ÷ readings expected, per building per day, stored in energy_daily and shown in reports.

# 8. Data volume, retention and performance

## 8.1 Size estimate

Example: 10 hotels, about 2,500 data points each (around 300 rooms with FCU and occupancy points, plus the plant, lighting, meters and other systems), read every 15 minutes.

| Item | Calculation | Result |
| --- | --- | --- |
| Readings per day | 10 buildings × 2,500 points × 96 readings | 2.4 million |
| Readings per year | 2.4 million × 365 | about 876 million |
| Raw size, uncompressed | about 90 bytes per reading including index | about 80 GB per year |
| Raw size, compressed (TimescaleDB) | typically 90% smaller after compression | about 8 to 10 GB per year |
| Hourly summaries | 10 × 2,500 × 24 × 365 | about 219 million rows per year |
| Daily summaries | 10 × 2,500 × 365 | about 9 million rows per year |
| Calculated energy (energy_interval) | 10 buildings × 28 systems × 96 × 365 | about 10 million rows per year |

Estimates only. Actual compression depends on the data; it should be measured with real readings during the pilot.

## 8.2 How long data is kept

| Data | Kept | Why |
| --- | --- | --- |
| Raw readings (ts.reading) | 2 years online, compressed after 7 days; then exported to archive storage | Detailed investigation and recalculation |
| Hourly summaries | 5 years | Trends, seasonal comparison |
| Daily and monthly results, KPIs | Permanently | Baselines, year-on-year savings, audits |
| Alarms and waste findings | 5 years | Fault history, proof of savings |
| Gateway heartbeats | 90 days | Recent connectivity only |
| Audit log and report log | At least 3 years (per company policy) | Traceability |

## 8.3 Performance

- ts.reading is a hypertable with weekly chunks; queries for "today" or "last 7 days" touch only one or two chunks.

- Index on (point_id, ts DESC) answers "latest value of each point" for live tiles.

- The dashboard reads energy_interval, energy_daily, kpi_value and the hourly summaries, never scanning raw readings for long periods.

- Indexes on alarm_event (building_id, status, start_ts) and waste_finding (building_id, status) keep the Faults and Insights pages fast.

# 9. Security and access

| Role | Sees | Can change |
| --- | --- | --- |
| Portfolio Manager | All buildings: energy, cost, KPIs, findings, reports | Finding status and owner, targets |
| Building Manager | Only assigned buildings (e.g. GRH) | Finding status for own buildings; acknowledge alarms |
| Control Room Operator | All buildings: live data, alarms, gateway health | Acknowledge alarms |
| Administrator | Everything | Master data, data points, tariffs, users |
| Ingest service (system account) | - | Insert readings and batches only; cannot read user data |
| Calculation jobs (system account) | Readings, context, master data | Write energy, KPI, finding, gap and alarm tables only |

- Row-level security on every table that has a building_id: a user's queries return only rows for buildings listed in app.user_building_access.

- Encryption: TLS for all connections (gateways and users); disk encryption at the data centre.

- Gateways authenticate with their own certificate or key; a gateway can only send data for its own building.

- No writes to the BMS: the gateways have read-only access to the BMS network.

- Backups: daily full backup plus continuous write-ahead log archiving (point-in-time recovery), with a restore test every quarter.

- Audit: every change to master data, targets, tariffs, and every alarm acknowledgement and report export is recorded in app.audit_log.

# 10. How the dashboard and reports use the tables

| Dashboard page / feature | Reads from |
| --- | --- |
| Portfolio Overview: tiles, building table, combined load profile | energy_interval, energy_daily, kpi_value, waste_finding, alarm_event, core.building |
| Building View: load profile by system, energy by system, system cards | energy_interval, kpi_value, reading (latest values), core.equipment |
| System Detail: equipment list, trend, KPIs | reading (latest), reading_hourly, kpi_value, waste_finding, core.equipment, core.data_point |
| Faults & Alerts: alarms, acknowledge, gateway health | alarm_event, gateway_status, data_gap |
| Energy Insights: heatmap, findings ranked by ₹/month | energy_interval (hour × day), waste_finding, waste_rule |
| Raw data view | reading, reading_hourly (BMS values without KPIs) |
| Reports (PDF) | energy_daily, energy_interval, kpi_value, waste_finding, alarm_event, energy_daily completeness; each report logged in app.report_log |
| Login and building selector | app.app_user, app.user_building_access |

In the demo, the simulator plays the part of the gateways and the calculation jobs. Replacing it with the real database changes the data source only; the pages stay the same.

# 11. Next steps

- Get the BMS point list from each building (BACnet / Modbus export) and map every point to a standard tag and a data point row.

- Collect the static data: areas, equipment list with rated power and capacity, meter tree, schedules, tariffs, and 12 months of past bills for the baseline.

- Confirm the reading interval (15 minutes recommended) and the gateway buffer size with the provider.

- Pilot with one building: create the database, load its point list, run one month of data, and measure the real volume and compression.

- Agree retention periods and access roles with IT and management.

- Later phase: add the maintenance data points ("Kept for future maintenance use") as new data points; no table changes are needed.